STUDY ON THE GROUNDWATER POTENTIAL EVALUATION AND MANAGEMENT

PLAN FOR THE SOUTHEAST KALAHARI (STAMPRIET) ARTESIAN BASIN

IN THE REPUBLIC OF NAMIBIA

## Japan International Co-operation Agency

### JICA Study Team

# EVALUATION OF TEST PUMPING DATA

Boreholes

J4-N (WW 39847)

Okonjama

| Box 86386 Windhoek Namibia | METZGER PM DRILLING Box 11733 Windhoek Namibia |
| --- | --- |

Windhoek

July 2000

1.	PUMPING TEST ANALYSIS

## J4-N (WW39847) - Pumping well

J4-A (WW39846)- Observation well

J4-K (WW39845)- Observation well

1.1.	Well Efficiency (Step draw down test) (Annex 1)

Well Efficiency was analysed by making use of the Jacob method for draw down data. Aquifer parameters used for the calculation of well efficiency were obtained from the evaluation results of the constant discharge test, which is discussed in Section 1.2 below.

The well efficiencies at the range of pumping rates used during the step draw down test are summarised in Table 1 below. Only four of the five steps were utilised for the evaluation of the borehole efficiency.

Table 1:  J4-N; Borehole efficiency at various pumping rates

| Borehole number | Step | Abstraction Rate [m3/h] | Draw Down* [m] | Borehole Efficiency [%] |
| --- | --- | --- | --- | --- |
| J4-N | 1 | 5 | 12.0 | 79.7 |
|  | 2 | 10 | 22.0 | 79.1 |
|  | 3 | 15 | 29.7 | 78.5 |
|  | 4 | 20 | 50.6 | 77.9 |

* modelled draw down using the Jacob analysis method

Data on the linear and non-linear well losses and skin factors as well as the efficient well radius are presented in Annex 1.

1.2.	Constant Discharge Test Analysis (Annex 2 - 6)

The constant discharge draw down curve of abstraction borehole J4-N indicates leakage. For leaky aquifers, the Walton Hantush analysis method with draw down and recovery data was once again used to calculate the hydraulic conductivity of the aquifer and the aquitard (Annex 2 & 3).

Aquifer storativity was once again estimated due to the fact that the observation boreholes J4-A and J4-K are located in the Auob sandstone and Kalahari sediments respectively.  During the duration of the constant discharge test, only a minor drop in the water level of the two observation boreholes at late times is observed.  This scenario could be due to leakage caused by pressure release in the underlying Nossob confined aquifer or due to natural oscillations in the groundwater table (See Annex 5).

The occurrence of leakage into the Nossob aquifer during abstraction could be due to water derived from storage within the overlying aquitard.  The results of the constant discharge analysis are summarised in Table 2 below.

Table 2:  Aquifer Parameters calculated for J4-N; Nossob sandstone

| Borehole number | Analysis Method | T | s | k | S | Simulation model | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | [m2/day] | [m] | [cm/sec] | [-] |  |  |
| J4-N | Walton-Hantush -draw down | 7.01 | 50 | 1,6 x 10-4 | *5 x 10-5 | Hantush | *Storativity estimated - Observation borehole not located in the tested aquifer |
|  | Walton-Hantush -recovery | 7.60 | 50 | 1,8 x 10-4 | *5 x 10-5 |  |  |

The Hantush model for leaky condition from aquitard storage was used to simulate and verify the actual data and analysis approach of the constant discharge test.  Simulation parameters summarised in Table 2 were used in simulation of the actual pumping test data (See Annex 4 for simulation results).

Annex 6 compares the draw down results of the pumping borehole J4-N and observation boreholes J4-A and J4-K and it is clear that pumping from the Nossob sandstone did not have much of an influence on the Auob sandstone and Kalahari aquifers.

The radius of influence (R) was estimated after SICHARDT (1928) using the equation:

R = 3000 x s x Kf 1/2

R = 3000 x 55.3 x 1.3 x 10-3 = 223 m

where

R = Radius of influence

s = Draw down in abstraction borehole at end of pumping

Kf = Permeability of the aquifer

The equation is approximately correct for unconfined aquifers. In case of a confined aquifer the radius of influence most probably larger and the 223 m are considered to be the minimum value.

A proper evaluation of R (and storativity S) will only be possible once reliable data from observation wells, penetrating the same aquifer as the pumped well, are available.

linear aquifer loss

linear well loss

non-linear well loss

Linear aquifer loss

Linear well loss

Non-linear well loss

J4-A

J4-K

Distance to observation borehole:  J4-A = 69 m;  J4-K = 129 m

Distance to observation borehole:  J4-A = 69 m;  J4-K = 129 m

J4-A

J4-K

J4-N