STUDY ON THE GROUNDWATER POTENTIAL EVALUATION AND MANAGEMENT

PLAN FOR THE SOUTHEAST KALAHARI (STAMPRIET) ARTESIAN BASIN

IN THE REPUBLIC OF NAMIBIA

## Japan International Co-operation Agency

### JICA Study Team

# EVALUATION OF TEST PUMPING DATA

Borehole

J7-K (WW39852)

Jackalsdraai

| Box 86386 Windhoek Namibia | METZGER PM DRILLING Box 11733 Windhoek Namibia |
| --- | --- |

Windhoek

September 2000

- PUMPING TEST ANALYSIS

J7-K (WW39852) - Pumping well

J7-N (WW39853) - Observation well

J7-Huis - Observation well

J7-Wind – Observation well

1.1.	Well Efficiency (Step Drawdown Test) (Annex 1)

Well Efficiency was analysed by making use of the Jacob method for draw down data. Aquifer parameters used for the calculation of well efficiency were obtained from the evaluation results of the constant discharge test, which is discussed in Section 1.2 below.

The well efficiencies at the range of pumping rates used during the step drawdown test are summarised in Table 1 below.

Table 1:	J6-K: Borehole efficiency at various pumping rates

| Borehole number | Step | Abstraction Rate [m3/h] | Draw Down* [m] | Borehole Efficiency [%] |
| --- | --- | --- | --- | --- |
| J7-K | 1 | 3.0 | 3.36 | 53.2 |
|  | 2 | 6.1 | 6.82 | 52.6 |
|  | 3 | 9.0 | 9.63 | 52.0 |
|  | 4 | 12.1 | 13.60 | 51.3 |

* modelled draw down using the Rorabaugh analysis method

Data on the linear and non-linear well losses and skin factors as well as the efficient well radius are presented in Annex 1.

1.2.	Constant Discharge Test Analysis (Annex 2 - 5)

The abstraction rate of the constant discharge test was 7 m3/h. The constant discharge draw down curve of abstraction borehole J7-K indicates leaky conditions. For leaky aquifers, the Walton / Hantush I analysis method with draw down and recovery data was used to calculate the hydraulic conductivity of the aquifer and the aquitard as well as the leakage factor B (Annex 2 & 3).  Using the normal Theis or Cooper-Jacob analysis will result in the over estimation of the hydraulic conductivity of the leaky aquifer and an under estimation of the hydraulic conductivity of the aquitard. (Kruseman, De Ridder, 1992).

The occurrence of leakage could be due to water derived from storage within the aquitard.  The sandstone within the Rietmond Formation is confined and under higher hydraulic pressure and will also contribute to leakage occurring into the upper Kalahari aquifer. The results of the constant discharge analysis are summarised in Table 2 below.

During the duration of the constant discharge test, a slight rise in the water level of observation borehole J7-N was observed, while the water level of J7-Wind fluctuated due to the borehole being pumped for water supply to the farm house (See Annex 5.1).

The water level of J7-Huis was clearly affected by the abstraction from J7-K. The observation borehole is located at a distance of 230 m and a maximum draw down of 0.6 m was observed after 72 hours pumping (See Annex 5.2). The draw down curve was analysed for transmissivity and storativity values. The transmissivity was calculated as T = 68 m2/day, while the storativity was calculated as S = 0.00023, which is a typical value for confined and leaky aquifers. The transmissivity is double the transmissivity calculated for the pumping borehole J7-K. However, the draw down curve is also affected by pumping of J7-K, which is about 150 m away. The draw down curve is therefore rather ‘bumpy’ (See Annex 3.1). This must be born in mind when utilising the calculated aquifer parameter obtained from observation borehole J7-Huis.

Table 2:	 Aquifer Parameters calculated for J7-K; Kalahari

| Borehole number | Analysis method | T | s | k | S | Comments |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | [m2/day] | [m] | [cm/sec] | [-] |  |
| J7-K | Walton / Hantush I -draw down | 30 | 30 | 1.2 x 10-3 | *5 x 10-3 | *Storativity estimated |
|  | Walton / Hantush I -recovery | 32 | 30 | 1.2 x 10-3 | *5 x 10-3 |  |
|  | Walton / Hantush I -draw down from observation borehole J7-Huis | 68 | 30 | 2.6 x 10-3 | 2 x 10-4 | Storativity calculated |

The Walton / Hantush I model for leaky condition from aquitard storage was used to simulate and verify the actual data and analysis approach of the constant discharge test.  Simulation parameters summarised in Table 2 were used in simulation of the actual pumping test data (See Annex 4 for simulation results).

The radius of influence (R) was estimated after SICHARDT (1928) using the equation:

R = 3000 x s x Kf 1/2

R = 3000 x 10.14 x 5 x 10-3 = 155 m

where

R = Radius of influence

s = Draw down in abstraction borehole at end of pumping

Kf = Permeability of the aquifer

The equation is approximately correct for unconfined aquifers. In case of a confined aquifer the radius of influence most probably larger and the 155 m are considered to be the minimum value. A draw down of 0.6 m was measured in observation borehole J7-Huis at a distance of 230 m. A more realistic value for R, namely 310 m, is double the calculated value of 155 m.

Linear aquifer loss

Linear well loss

Non-linear well loss

Data on the linear and non-linear well losses and skin factors as well as the efficient well radius are presented in Annex 2.1.

Annex 2

Annex 3

J7-N

J7-Wind

J7-K

Distance of observation boreholes:   JK-N = 56.2 m;     Jk-Wind = 320 m

Distance of observation borehole:   JK-Huis = 230 m

J7-K

J7-Huis