STUDY ON THE GROUNDWATER POTENTIAL EVALUATION AND MANAGEMENT

PLAN FOR THE SOUTHEAST KALAHARI (STAMPRIET) ARTESIAN BASIN

IN THE REPUBLIC OF NAMIBIA

## Japan International Co-operation Agency

### JICA Study Team

# EVALUATION OF TEST PUMPING DATA

Borehole

J9-A (WW39857)

Klein Swart Modder

| Box 86386 Windhoek Namibia | METZGER PM DRILLING Box 11733 Windhoek Namibia |
| --- | --- |

Windhoek

October 2000

- PUMPING TEST ANALYSIS

J9-A (WW39857) - Pumping well (sub-artesian)

J9 (WW31759) - Observation well (sub-artesian)

J9 (WW245) - Observation well (artesian)

1.1.	Well Efficiency (Step Drawdown Test) (Annex 1)

Well Efficiency was analysed by making use of the Jacob method for draw down data. Aquifer parameters used for the calculation of well efficiency were obtained from the evaluation results of the constant discharge test, which is discussed in Section 1.2 below.

The well efficiencies at the range of pumping rates used during the step drawdown test are summarised in Table 1 below.

Table 1:	J9-A; borehole efficiency at various pumping rates

| Borehole number | Step | Abstraction Rate [m3/h] | Draw Down* [m] | Borehole Efficiency [%] |
| --- | --- | --- | --- | --- |
| J9-A | 1 | 15 | 0.59 | 85.9 |
|  | 2 | 25 | 0.39 | 64.8 |
|  | 3 | 35 | 1.14 | 52.1 |
|  | 4 | 45 | 2.72 | 43.5 |

* at cut-off time ∆t, after which well bore storage has no affect on the well performance

Data on the linear and non-linear well losses and skin factors as well as the efficient well radius are presented in Annex 1.

1.2.	Constant Discharge Test Analysis (Annex 2 - 6)

An abstraction rate of 46 m3/h was applied for the constant discharge test. The constant discharge draw down curve of abstraction borehole J9-A indicates confined conditions. For confined aquifers, the Theis analysis method with draw down and recovery data was used to calculate the hydraulic conductivity of the aquifer (Annex 2 & 3). The recovery data shows higher transmissivity values. In addition the transmissivity and storativity was calculated from the draw down curve of the observation borehole WW31759 (Annex 4). The observation borehole was affected by the pumping from J9-A and showed a draw down of approximately 20 cm after 3-days pumping (Annex 5). Again, the transmissivity was higher than the evaluated values of the pumping borehole, indicating some increase in transmissivity away from J9-A. The order of magnitude, however, is the same in all cases.

The additional pumping from the farm borehole WW245, which penetrates the same aquifer, most probably influenced the draw down curve of WW31759.

The results of the constant discharge analysis are summarised in Table 2 below.

Table 2:	Aquifer Parameters calculated for J9-A; Auob sandstone

| Borehole number | Analysis Method | T | s | kf | S | Simulation model |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | [m2/day] | [m] | [cm/sec] | [-] |  |
| J9-A | Theis-draw down | 1,240 | 75 | 1.9 x 10-2 | *5 x 10-5 | Theis |
|  | Theis-recovery | 1,640 | 75 | 2.5 x 10-2 | *5 x 10-5 |  |
|  | Theis-draw down Obs. BH WW31759 | 2,160 |  |  | 3 x 10-4 |  |

*estimated

The Theis model for confined aquifer conditions was used to simulate and verify the actual data and analysis approach of the constant discharge test.  No leaky conditions could be evaluated for J9-A. Simulation parameters summarised in Table 2 were used in simulation of the actual pumping test data (See Annex 5 for simulation results).

Annex 6 compares the draw down results of the pumping borehole J9-A and observation borehole WW31759.

The radius of influence (R) was estimated after SICHARDT (1928) using the equation:

R = 3000 x s x Kf 1/2

R = 3000 x 2.84 x 0.018 = 156 m

where

R = Radius of influence

s = Draw down in abstraction borehole at end of pumping

Kf = Permeability of the aquifer

The equation is approximately correct for unconfined aquifers. In case of a confined aquifer the radius of influence is larger and the 156 m are considered to be the minimum value.

The reaction of the water level in observation borehole WW31759 shows that the actual radius of influence is much lager than the above estimate. R is estimated to be greater than 500 m.

.

Data on the linear and non-linear well losses and skin factors as well as the efficient well radius are presented in Annex 2.1.

WW31759

J9-A

Distance to observation borehole WW31759 = 425 m